## datacentres_20260810091044
Energie-efficiëntie datacentra 2026 (gegevens 2025) 5/10/2026
referenceId | operator_name | operator_email | name | lauCode | > 500 kW | type | operational StartYear | operational StartMonth | electricInfrastructure RedundancyLevel | electricInfrastructure RedundancyLevelDetails | coolingInfrastructure RedundancyLevel | coolingInfrastructure RedundancyLevelDetails | itPowerDemand Installed | itPowerDemand Installed_unit | itPowerDemand InstalledType | totalFloorArea | totalFloorArea unit | totalComputerRoom FloorArea | totalComputerRoom FloorArea_unit | totalEnergy Consumption | totalEnergy Consumption_unit | totalEnergy FromBackup Consumption | totalEnergy FromBackup Consumption_unit | totalEnergy ITEquipment Consumption | totalEnergy ITEquipment Consumption_unit | electrical GridFunctions | electrical GridFunction Other | average BatteryCapacity | average BatteryCapacity unit | total WaterInput | total WaterInput unit | total WaterInput Methodology | totalPotable WaterInput | totalPotable WaterInput unit | wasteHeat Reused | wasteHeat Reused_unit | averageWaste Temperature | averageWaste Temperature_unit | averageSetPoint Temperature | averageSetPoint Temperature_unit | refrigerantType | other RefrigerantType | cooling DegreeDays | cooling DegreeDays unit | totalRenewable EnergyConsumption | totalRenewable EnergyConsumption_unit | totalRenewable EnergyConsumption GuaranteesOfOrigin | totalRenewable EnergyConsumption GuaranteesOfOrigin_unit | totalRenewable EnergyConsumption PowerPurchasingAgreements | totalRenewable EnergyConsumption PowerPurchasingAgreements_unit | totalRenewable EnergyConsumption OnSite | totalRenewable EnergyConsumption OnSite_unit | additional Comments Energy | ictServers Capacity | ictServers Capacity_unit | ictStorage Capacity | ictStorage Capacity_unit | ictStorage Capacity Coverage | ictStorage Capacity Coverage_unit | ictServers Capacity Coverage | ictServers Capacity Coverage_unit | incoming Bandwidth | incoming Bandwidth_unit | outgoing Bandwidth | outgoing Bandwidth_unit | incoming Data | incoming Data_unit | outgoing Data | outgoing Data_unit | additional Comments Capacity
NL-001 | QTS Groningen ¦ DC1 B.V. |  | QTS Groningen DC1 | GM0014 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2001 | January
NL-002 | QTS Eemshaven ¦ DC1 B.V. |  | QTS Eemshaven DC1 | GM1966 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2007 | October
NL-003 | QTS Eemshaven DC2 |  | QTS Eemshaven DC2 | GM1966 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2026 | September
NL-01 | EdgeConneX |  | AMS01 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2016 | July
NL-02 | EdgeConneX |  | AMS02 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2016 | December | [9 empty] | 4622 | M2
NL-03 | EdgeConneX |  | AMS03 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2018 | January
NL-04 | EdgeConneX |  | AMS04 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2019 | November | [17 empty] | OTHER
NL-05 | EdgeConneX |  | AMS05 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2022 | September
NL-06 | EdgeConneX |  | AMS06 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2023 | October
NL-1119NM71 | Orange Business Netherlands |  | Orange Business Netherlands | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 1995 | January | 2N | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 400 | KW | INSTALLED | 2428 | M2 | 1533 | M2 | 1244155 | KWH | 0 | KWH | 0 | KWH | FREQUENCY_RESPONSE |  | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | Glycol 35% | 0 | DEGREE_DAYS | 0 | KWH | 0 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-2601 | ICT Shared Service Centre |  | Snellius | GM0546 | Ja | ENTERPRISE_DATA_CENTRE_SINGLE_STRUCTURE | 2024 | August
NL-AER-01 | NorthC Datacenters B.V. |  | NorthC Datacenters Almere | GM0034 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | December | 2N | AT_RACK_LEVEL | N+2 | AT_ROOM_LEVEL |  |  | RATED | 26000 | M2 | 6870 | M2 | [7 empty] | Geen | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 27.6 | DEGREE_CELSIUS | 26.9 | DEGREE_CELSIUS | R_134A |  | 22 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons onbekend.
NL-AM1 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM1 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | January | N+1 |  | N+1 |  |  |  | RATED | 8980 | M2 | 4750 | M2 | [6 empty] | OTHER | none | [15 empty] | 34 | DEGREE_DAYS
NL-AM2 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM2 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2011 | April | N+1 |  | N+1 |  |  |  |  | 8982 | M2 | 4150 | M2 | [13 empty] | 37508 | M3 | [8 empty] | 34 | DEGREE_DAYS |  |  |  |  | 0 | KWH
NL-AM3 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM3 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2012 | September | N+1 |  | N+1 |  |  |  |  | 25708 | M2 | 12600 | M2 | [6 empty] | OTHER | none | 0 | KW | [13 empty] | 34 | DEGREE_DAYS
NL-AM4 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM4 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2017 | October | N+1 |  | N+1 |  |  |  |  | 25708 | M2 | 12600 | M2 | [7 empty] | none |  |  |  |  | CATEGORY_1 | [10 empty] | 34 | DEGREE_DAYS |  |  |  |  | 0 | KWH | 0 | KWH
NL-AM5 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM5 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2012 | January | N+1 |  | N+1 |  |  |  |  | 13750 | M2 | 7320 | M2 | [12 empty] | CATEGORY_1 | [6 empty] | 27 | DEGREE_CELSIUS |  |  | 34 | DEGREE_DAYS
NL-AM6 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM6 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2015 | November | N+1 |  | N+1 |  |  |  |  | 19000 | M2 | 6990 | M2
NL-AM7 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM7 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 1999 | December | N+1 |  | N+1 |  |  |  |  | 20864 | M2 | 16938 | M2 | [23 empty] | 34 | DEGREE_DAYS
NL-AM8 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM8 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2001 | January | N+1 |  | N+1 |  |  |  |  | 6614 | M2 | 3400 | M2 | [8 empty] | 0 | KW | [13 empty] | 34 | DEGREE_DAYS
NL-AM9 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | AM11 | GM0363 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2011 | January
NL-AMS | Global Switch |  | Global Switch Amsterdam | GM0363 | Ja | COLOCATION_DATA_CENTRE_GROUP_OF_STRUCTURES | 1998 | January | 2N | AT_RACK_LEVEL | N+2 | AT_RACK_LEVEL |  |  | INSTALLED | [10 empty] | OTHER | [5 empty] | CATEGORY_1 |  |  | 0 | KWH | 0 | DEGREE_CELSIUS | 0 | DEGREE_CELSIUS |  |  | 45 | DEGREE_DAYS | 0 | KWH | 0 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-AMS-01 | NorthC Datacenters B.V. |  | NorthC Datacenters Amsterdam | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 1999 | June | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL |  |  | RATED | 5000 | M2 | 2500 | M2 | [6 empty] | OTHER | Geen | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 0 | DEGREE_CELSIUS | 26.4 | DEGREE_CELSIUS | OTHER | Geen | [6 empty] | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons onbekend.
NL-AMS-02 | NorthC Datacenters B.V. |  | NorthC Amsterdam 2 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2000 | January | N+1 | AT_RACK_LEVEL | N+1 | AT_RACK_LEVEL |  |  | INSTALLED | 9625 | M2 | 5900 | M2 | [6 empty] | OTHER | NVT | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 22.3 | DEGREE_CELSIUS | 28.2 | DEGREE_CELSIUS | R_410A |  | 17 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons niet bekend.
NL-AMS1 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter Amsterdam 1 | GM0394 | Nee | COLOCATION_DATA_CENTRE_GROUP_OF_STRUCTURES_WITH_CO_HOSTING_SERVICES | 2020 | May
NL-AMS10 | Interxion Nederland BV | osalami@digitalrealty.com | AMS10 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2019 | December | 2N | AT_HIGH_VOLTAGE_LEVEL | N+2 | AT_ROOM_LEVEL | 31450 | KW | INSTALLED | 48868 | M2 | 14390 | M2 | 166896011 | KWH | 477297 | KWH | 147854182 | KWH | OTHER | N/A | 0 | KW | 1353 | M3 | CATEGORY_1 | 1353 | M3 | 0 | KWH | 29 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_134A |  | 79 | DEGREE_DAYS | 166418714 | KWH | 123149848 | KWH | 43268866 | KWH | 0 | KWH |  | 109670.56 | THOUSANDS | 371.86 | PB | 3 | PERCENT | 3 | PERCENT | 2454.31 | GB | 2464.17 | GB | 246.97 | EB | 191.07 | EB
NL-AMS15 | Digital Hoofddorp BV | osalami@digitalrealty.com | AMS15 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2017 | July | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 14000 | KW | INSTALLED | 33452 | M2 | 7232 | M2 | 83735150 | KWH | 136712 | KWH | 68576187 | KWH | OTHER | N/A | 0 | KW | 52148 | M3 | CATEGORY_1 | 52148 | M3 | 0 | KWH | 39 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_410A |  | 79 | DEGREE_DAYS | 83598438 | KWH | 61862844 | KWH | 21735594 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-AMS16 | Digital Hoofddorp 2 BV | osalami@digitalrealty.com | AMS16 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2017 | October | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 2000 | KW | INSTALLED | 35816 | M2 | 6564 | M2 | 9086800 | KWH | 4887 | KWH | 6112535 | KWH | OTHER | N/A | 0 | KW | 1658 | M3 | CATEGORY_1 | 1658 | M3 | 0 | KWH | 39 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_410A |  | 79 | DEGREE_DAYS | 9081913 | KWH | 6720616 | KWH | 2361297 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-AMS17 | Digital Realty Netherlands 11 BV | osalami@digitalrealty.com | AMS17 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2016 | July | 2N | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 7000 | KW | INSTALLED | 14258 | M2 | 7630 | M2 | 41235621 | KWH | 29359 | KWH | 33410149 | KWH | OTHER | N/A | 0 | KW | 1143 | M3 | CATEGORY_1 | 1143 | M3 | 0 | KWH | 30 | DEGREE_CELSIUS | 25 | DEGREE_CELSIUS | OTHER | R410A, R134A | 79 | DEGREE_DAYS | 41206262 | KWH | 30492634 | KWH | 10713628 | KWH | 0 | KWH |  | 741727.38 | THOUSANDS | 88.12 | PB | 1 | PERCENT | 1 | PERCENT | 44944.01 | GB | 44937.14 | GB | 84.64 | EB | 97.59 | EB
NL-AMS18 | Digital Realty Netherlands 11 BV | osalami@digitalrealty.com | AMS18 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2009 | March | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 6000 | KW | INSTALLED | 13915 | M2 | 2709 | M2 | 23076105 | KWH | 12566 | KWH | 14150561 | KWH | OTHER | N/A | 0 | KW | 15935 | M3 | CATEGORY_1 | 15935 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 25 | DEGREE_CELSIUS | OTHER | R134A, R410A, R407C | 79 | DEGREE_DAYS | 23063539 | KWH | 17067019 | KWH | 5996520 | KWH | 0 | KWH |  | 595124.77 | THOUSANDS | 2715.28 | PB | 5 | PERCENT | 5 | PERCENT | 1703.03 | GB | 1436.59 | GB | 35.25 | EB | 73.42 | EB
NL-AMS3 | Interxion Nederland BV | osalami@digitalrealty.com | AMS03 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 1999 | December | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 2710 | KW | INSTALLED | 13422 | M2 | 3142 | M2 | 14617828 | KWH | 13000 | KWH | 9928586 | KWH | OTHER | N/A | 0 | KW | 506 | M3 | CATEGORY_1 | 506 | M3 | 0 | KWH | 34 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | R410A, R134A, R407C | 79 | DEGREE_DAYS | 14604828 | KWH | 10807573 | KWH | 3797255 | KWH | 0 | KWH |  | 57919.14 | THOUSANDS | 49.09 | PB | 11 | PERCENT | 11 | PERCENT | 1325.26 | GB | 2942.74 | GB | 3.81 | EB | 9.02 | EB
NL-AMS5 | Interxion Nederland BV | osalami@digitalrealty.com | AMS05 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | December | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 6900 | KW | INSTALLED | 19537 | M2 | 4322 | M2 | 32844798 | KWH | 109537 | KWH | 23122897 | KWH | OTHER | N/A | 0 | KW | 1426 | M3 | CATEGORY_1 | 1426 | M3 | 0 | KWH | 32 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | R134A, R407C, R513A | 79 | DEGREE_DAYS | 32735261 | KWH | 24224093 | KWH | 8511168 | KWH | 0 | KWH |  | 88132.97 | THOUSANDS | 177.28 | PB | 8 | PERCENT | 8 | PERCENT | 1905.04 | GB | 1945.31 | GB | 3.18 | EB | 3.7 | EB
NL-AMS6 | Interxion Nederland BV | osalami@digitalrealty.com | AMS06 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2012 | September | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 10300 | KW | INSTALLED | 19297 | M2 | 4436 | M2 | 69054394 | KWH | 136495 | KWH | 51991592 | KWH | OTHER | N/A | 0 | KW | 2003 | M3 | CATEGORY_1 | 2003 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | R410A, R134A, R1234ze | 79 | DEGREE_DAYS | 68917899 | KWH | 50999245 | KWH | 17918654 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-AMS7 | Interxion Nederland BV | osalami@digitalrealty.com | AMS07 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2014 | March | 2N | AT_HIGH_VOLTAGE_LEVEL | N+2 | AT_ROOM_LEVEL | 15000 | KW | INSTALLED | 36142 | M2 | 8229 | M2 | 32676659 | KWH | 229895 | KWH | 23750761 | KWH | OTHER | N/A | 0 | KW | 2213 | M3 | CATEGORY_1 | 2213 | M3 | 0 | KWH | 35 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | R410A, R134A | 79 | DEGREE_DAYS | 32446764 | KWH | 24010605 | KWH | 8436159 | KWH | 0 | KWH |  | 378073.95 | THOUSANDS | 138.39 | PB | 5 | PERCENT | 5 | PERCENT | 4816 | GB | 5000.59 | GB | 9.84 | EB | 15.22 | EB
NL-AMS8 | Interxion Nederland BV | osalami@digitalrealty.com | AMS08 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2016 | December | 2N | AT_HIGH_VOLTAGE_LEVEL | N+2 | AT_ROOM_LEVEL | 14800 | KW | INSTALLED | 38030 | M2 | 8208 | M2 | 87914947 | KWH | 130317 | KWH | 76810348 | KWH | OTHER | N/A | 0 | KW | 538 | M3 | CATEGORY_1 | 538 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | R410A, R134A | 79 | DEGREE_DAYS | 87784630 | KWH | 64960626 | KWH | 22824004 | KWH | 0 | KWH |  | 0 | THOUSANDS | 4968.81 | PB | 0 | PERCENT | 0 | PERCENT | 472.2 | GB | 699.56 | GB | 195.88 | EB | 307.8 | EB
NL-AMS9 | Interxion Science Park BV | osalami@digitalrealty.com | AMS09 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2017 | March | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 2500 | KW | INSTALLED | 4902 | M2 | 2632 | M2 | 11870576 | KWH | 13892 | KWH | 8488997 | KWH | OTHER | N/A | 0 | KW | 624 | M3 | CATEGORY_1 | 624 | M3 | 0 | KWH | 30 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | HFC-134a, R410A | 79 | DEGREE_DAYS | 11856684 | KWH | 8773946 | KWH | 3082738 | KWH | 0 | KWH |  | 341788.59 | THOUSANDS | 243.59 | PB | 6 | PERCENT | 6 | PERCENT | 31448.89 | GB | 31063.21 | GB | 2527.43 | EB | 5449.03 | EB
NL-AMSESG1 | Microsoft Datacenter Nederland B.V. | ESG-NL@microsoft.com | AMSESG1 | GM1911 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2015 | July | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 188200 | KW | RATED | 95833 | M2 | 68111 | M2 | 1167354853 | KWH | 1048290 | KWH | 1018182622 | KWH | OTHER | N.A. | 0 | KW | 31071 | M3 | CATEGORY_1 | 31071 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 29.4 | DEGREE_CELSIUS | R_410A |  | 34 | DEGREE_DAYS | 1166306562 | KWH | 0 | KWH | 1166306562 | KWH | 0 | KWH
NL-AMSESG2 | Microsoft Datacenter Nederland B.V. | ESG-NL@microsoft.com | AMSESG2 | GM1911 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2024 | June | N+1 | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 82000 | KW | RATED | 47565 | M2 | 26382 | M2 | 177890508 | KWH | 141428 | KWH | 141548143 | KWH | OTHER | N.A. | 0 | KW | 6072 | M3 | CATEGORY_1 | 6072 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 29.4 | DEGREE_CELSIUS | OTHER | N.A. | 34 | DEGREE_DAYS | 177749080 | KWH | 0 | KWH | 177749080 | KWH | 0 | KWH | [17 empty] | N.A.
NL-ARN1 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter Arnhem 1 | GM0202 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2010 | June
NL-Best | Rabobank |  | Datacenter Best | GM0753 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2007 | March | 2N | AT_HIGH_VOLTAGE_LEVEL | 2N | AT_ROOM_LEVEL | 1400 | KW | INSTALLED | 26060 | M2 | 5830 | M2 | 14416590 | KWH | 70000 | KWH | 9184743 | KWH | OTHER | geen | 0 | KW | 2452 | M3 | CATEGORY_1 | 2452 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 22 | DEGREE_CELSIUS | OTHER | R-134A en R1234ZE | 192 | DEGREE_DAYS | 14416590 | KWH | 14416590 | KWH | 14416590 | KWH | 0 | KWH | Geen
NL-BIT-2BCD | BIT BV | info@bit.nl | BIT-2BCD | GM0228 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2006 | January | 2N | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 0 | KW | INSTALLED | 1300 | M2 | 1200 | M2 | 8556145 | KWH | 16736 | KWH | 6470288 | KWH | PEAK_DEMAND |  | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 51812 | KWH | 20 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | Er worden verschillende koudemiddelen gebruik. | 3527 | DEGREE_DAYS | 8531118 | KWH | 8404005 | KWH | 0 | KWH | 127113 | KWH
NL-Boxtel | Rabobank |  | Datacenter Boxtel | GM0757 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2010 | April | 2N | AT_HIGH_VOLTAGE_LEVEL | 2N | AT_ROOM_LEVEL | 800 | KW | INSTALLED | 21878 | M2 | 6500 | M2 | 10886812 | KWH | 137124 | KWH | 5406981 | KWH | OTHER | Geen | 0 | KW | 21009 | M3 | CATEGORY_1 | 21009 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 22 | DEGREE_CELSIUS | OTHER | R-134A en R515B | 192 | DEGREE_DAYS | 10886812 | KWH | 10886812 | KWH | 10886812 | KWH | 0 | KWH | Geen
NL-BRB1 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter NL Zuid-West 1 | GM0867 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2012 | January
NL-BRB2 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter NL Zuid-West 2 | GM0851 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2006 | January
NL-C0001 | Cyrusone AMS 3 BV |  | Cyrusone AMS1 | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2020 | March | 2N high | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL | 27000 | KW | RATED | 26850 | M2 | 14675 | M2 | 36197890 | KWH | 163578 | KWH | 21207825 | KWH | OTHER | n.a. | 0 | KW | 1856 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 24 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | OTHER | HFC-134 | 11 | DEGREE_DAYS | 36034312 | KWH | 36034312 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-CBC-5334 | Rijksuniversiteit Groningen | sander.dijkstra@Rug.nl | Coenraad Bron Center Grouwelerie | GM0014 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2021 | September | Ja | AT_LOW_VOLTAGE_LEVEL | Ja | AT_ROOM_LEVEL | 515 | KW | INSTALLED | 609 | M2 | 487 | M2 | 4485822 | KWH | 10000 | KWH | 3115154 | KWH | OTHER | OTHER | 0 | KW | 91 | M3 | CATEGORY_1 | 91 | M3 | 0 | KWH | 34 | DEGREE_CELSIUS | 30 | DEGREE_CELSIUS | R_410A |  | 70 | DEGREE_DAYS | 107083 | KWH | 0 | KWH | 0 | KWH | 107083 | KWH | RUG heeft dit jaar geen GVO certificaten aangekocht. Bron koeldagen KWA https://www.kwa.nl | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 5 | GB | 5 | GB | 0 | EB | 0 | EB | Bandbreedte van DC's wordt niet gemonitored, bijgaand de totalen tot nu toe.
NL-DC1A | Green Box Computing BV | eemshaven@google.com | Green Box Computing BV Site | GM1966 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2016 | July | N+1 / 2N | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL |  |  | RATED | 173001 | M2 | 102736 | M2 | [6 empty] | OTHER | Not applicable | 0 | KW | 2001013 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 31.9 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_718 |  | 36 | DEGREE_DAYS | [6 empty] | 0 | KWH
NL-DC1B | Green Box Computing BV | eemshaven@google.com | Green Box Computing BV Site 2 | GM1895 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2025 | September | N+1 / 2N | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL |  |  | RATED | 15622 | M2 | 13042 | M2 | [6 empty] | OTHER | Not applicable | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 25.2 | DEGREE_CELSIUS | 25 | DEGREE_CELSIUS | OTHER | R1234ze | 67 | DEGREE_DAYS |  |  | 0 | KWH |  |  | 0 | KWH
NL-DC2-EHV | Interconnect |  | DC2 | GM0772 | Ja | CO_HOSTING_DATA_CENTRE_GROUP_OF_STRUCTURES_WITH_COLOCATION_SERVICES | 2011 | November
NL-DC3-DB | Interconnect |  | DC3 | GM0796 | Ja | CO_HOSTING_DATA_CENTRE_GROUP_OF_STRUCTURES_WITH_COLOCATION_SERVICES | 2023 | December | [13 empty] | 54481 | KWH | [25 empty] | 0 | KWH
NL-DFT-01 | NorthC Datacenters B.V. |  | NorthC Datacenters Delft | GM0503 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2012 | September | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL |  |  | RATED | 5000 | M2 | 1800 | M2 | [6 empty] | OTHER | Geen. | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 0 | DEGREE_CELSIUS | 26.9 | DEGREE_CELSIUS | OTHER | Geen | 29 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons onbekend.
NL-EIN-01 | NorthC Datacenters B.V. |  | NorthC Eindhoven | GM0772 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2015 | July | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL |  |  |  | 2500 | M2 | 1250 | M2 | [6 empty] | OTHER | Geen | 0 | KW |  |  | CATEGORY_1 |  |  |  |  | 28 | DEGREE_CELSIUS | 26.3 | DEGREE_CELSIUS | R_410A |  | 56 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons onbekend
NL-EIN-02 | NorthC Datacenters B.V. |  | NorthC Eindhoven 2 | GM0772 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2024 | April | 2N | AT_RACK_LEVEL | N+1 | AT_RACK_LEVEL |  |  | INSTALLED | 4000 | M2 | 2500 | M2 | [6 empty] | OTHER | NVT | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 25.8 | DEGREE_CELSIUS | 25.4 | DEGREE_CELSIUS | OTHER | R1234ZE | 56 | DEGREE_DAYS | [6 empty] | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons niet bekend.
NL-EN01 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | EN1 | GM0153 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | February | N+1 |  | N+1 | [31 empty] | 33 | DEGREE_DAYS
NL-GHDC1 | Greenhouse Datacenters |  | Greenhouse Datacenters DC1 | GM1783 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2013 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 700 | KW | INSTALLED | 1119 | M2 | 750 | M2 | 4362690 | KWH | 1813 | KWH | 3322688 | KWH | OTHER | n.v.t. | 0 | KW | 125 | M3 | CATEGORY_1 | 125 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 0 | DEGREE_CELSIUS | OTHER | Buitenlucht | 19 | DEGREE_DAYS | 2544903 | KWH | 2544903 | KWH | 0 | KWH | 0 | KWH | 0 | 291.6 | THOUSANDS | 317 | PB | 90 | PERCENT | 10 | PERCENT | 104 | GB | 0.3 | TB | 0.9 | ZB | 2.6 | ZB
NL-GHDC2 | Greenhouse Datacenters |  | Greenhouse Datacenters DC2 | GM1783 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2018 | May | 2N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 1500 | KW | INSTALLED | 2300 | M2 | 895 | M2 | 9918505 | KWH | 1867 | KWH | 8700443 | KWH | OTHER | n.v.t. | 0 | KW | 4060 | M3 | CATEGORY_1 | 4060 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 0 | DEGREE_CELSIUS | OTHER | Fresh Air + Watercooling | 19 | DEGREE_DAYS | 5785795 | KWH | 5785795 | KWH | 0 | KWH | 0 | KWH | - | 907.2 | THOUSANDS | 56.8 | PB | 90 | PERCENT | 10 | PERCENT | 999 | GB | 1.6 | TB | 8.7 | ZB | 14 | ZB
NL-GHDC3 | Greenhouse Datacenters |  | Greenhouse Datacenters DC3 | GM1783 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2025 | February | 2N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 1500 | KW | INSTALLED | 875 | M2 | 585 | M2 | 330567 | KWH | 353 | KWH | 166365 | KWH | OTHER | n.v.t. | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_513A |  | 19 | DEGREE_DAYS | 231397 | KWH | 231397 | KWH | 0 | KWH | 0 | KWH |  | 1350 | THOUSANDS | 1350 | PB | 90 | PERCENT | 10 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Alle verkeer loopt via DC2. Deze zijn dan ook ingevoerd bij DC2
NL-GM1674 | Colt Data Centre Services |  | Colt Data Centre Services | GM1674 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2013 | January | [44 empty] | -
NL-GRN1 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter Groningen 1 | GM0014 | Nee | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2018 | February
NL-GRQ-01-02 | NorthC Datacenters B.V. |  | NorthC Groningen 1 en 2 | GM0014 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2013 | June | 2N | AT_RACK_LEVEL | N+1 | AT_RACK_LEVEL |  |  | INSTALLED | 5533 | M2 | 3518 | M2 | [6 empty] | OTHER | NVT |  |  |  |  | CATEGORY_1 |  |  | 0 | KWH | 26.2 | DEGREE_CELSIUS | 26.5 | DEGREE_CELSIUS | R_32 |  | 21 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons niet bekend.
NL-GTDC | GTDC B.V. | OPSTeam4@switchdatacenters.com | Switch Datacenters AMS4 | GM0384 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2024 | January | N+1 | AT_RACK_LEVEL | N+2 | AT_ROOM_LEVEL | 14000 | KW | INSTALLED | 7560 | M2 | 4606 | M2 | 28288000 | KWH | 125189 | KWH | 22539883 | KWH | OTHER | N/A | 0 | KW | 387 | M3 | CATEGORY_1 | 387 | M3 | 0 | KWH | 34 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | OTHER | R410: R32: R1234ZE | 8 | DEGREE_DAYS | 28288000 | KWH | 28288000 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-H140-142 | Nikhef Housing | support@nikhefhousing.nl | Nikhef Housing | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 1992 | October | 2N | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 730 | KW | RATED | 900 | M2 | 800 | M2 | 7664511 | KWH | 4304 | KWH | 5895778 | KWH | OTHER | N/A | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 890016 | KWH | 25 | DEGREE_CELSIUS | 25 | DEGREE_CELSIUS | OTHER | combi van R134a en R1234ze | 105 | DEGREE_DAYS | 7664511 | KWH | 7664511 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Het dataverkeer is niet te meten. Daarom overal 0 ingevuld.
NL-Hurk-NZ | Atos | rob.vanvrede@atos.net | Atos Datacenter 'de Hurk' | GM0772 | Nee | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | January
NL-IR-AMS-1 | Iron Mountain (Nederland) Data Centre BV |  | AMS-1 | GM0392 | Ja | COLOCATION_DATA_CENTRE_GROUP_OF_STRUCTURES | 2007 | January | N+1, 2N | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 12924 | KW | RATED | 17754 | M2 | 8113 | M2 | 113652000 | KWH | 168661 | KWH | 82356521 | KWH | OTHER | Geen | 0 | KW | 124000 | M3 | CATEGORY_1 | 124000 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | OTHER | R_410A, R32 en water | 7 | DEGREE_DAYS | 113652000 | KWH | 113652000 | KWH | 8000000 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | De gevraagde informatie is ons niet bekend.
NL-KBW | Verizon Nederland B.V. | toby.demol@nl.verizon.com | KBW | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2001 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 768 | KW | RATED | 4045 | M2 | 2931 | M2 | 6424186 | KWH | 54000 | KWH | 3049656 | KWH | OTHER | geen | 0 | KW | 216 | M3 | CATEGORY_1 | 216 | M3 | 0 | KWH | 26 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | R_134A |  | 15 | DEGREE_DAYS | 6104354 | KWH | 5796955 | KWH | 0 | KWH | 307399 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 16 | GB | 16 | GB | 0.0064 | EB | 0.009 | EB
NL-MC-AMS01 | Franklin Hendriks |  | AMS01 maincubes B.V. | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2018 | January
NL-NAP | Verizon Nederland B.V. | toby.demol@nl.verizon.com | NAP | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2011 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+2 | AT_ROOM_LEVEL | 721 | KW | RATED | 3237 | M2 | 2640 | M2 | 6796451 | KWH | 124110 | KWH | 3241165 | KWH | OTHER | geen | 0 | KW | 363 | M3 | CATEGORY_1 | 363 | M3 | 0 | KWH | 26 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | R_134A |  | 15 | DEGREE_DAYS | 6311292 | KWH | 6311292 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 22 | GB | 22 | GB | 0 | EB | 0 | EB
NL-NDHR-1 | Yondr Netherlands B.V. |  | NDHR-1 | GM1911 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2020 | February | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL |  |  |  | 30185 | M2 | [9 empty] | n/a | [7 empty] | 0 | KWH | 34 | DEGREE_CELSIUS | 26 | DEGREE_CELSIUS | R_410A |  | 61 | DEGREE_DAYS
NL-NL1 | Serverius B.V. |  | Kolodc NL1 Dronten | GM0303 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2010 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 814 | KW | RATED | 1652 | M2 | 855 | M2 | 9572945 | KWH | 0 | KWH | 7176121 | KWH | OTHER | Normal usage | 0 | KW | 59 | M3 | CATEGORY_1 | 59 | M3 | 0 | KWH | 29.5 | DEGREE_CELSIUS | 21.7 | DEGREE_CELSIUS | R_410A |  | 23 | DEGREE_DAYS | 1111991 | KWH | 957295 | KWH | 0 | KWH | 154696 | KWH
NL-NL2 | Serverius B.V. |  | KoloDC NL2 Meppel | GM0119 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2014 | March | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 710 | KW | RATED | 1243 | M2 | 529 | M2 | 8562568 | KWH | 5345 | KWH | 6296006 | KWH | OTHER | Normal usage | 0 | KW | 941 | M3 | CATEGORY_1 | 941 | M3 | 0 | KWH | 28.3 | DEGREE_CELSIUS | 22 | DEGREE_CELSIUS | OTHER | R410A + R407C +R454B | 19 | DEGREE_DAYS | 866442 | KWH | 856257 | KWH | 0 | KWH | 10185 | KWH
NL-NL3-Sev | Serverius B.V. |  | KoloDC NL3 Apeldoorn | GM0200 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2019 | October | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 504 | KW | RATED | 975 | M2 | 208 | M2 | 2626739 | KWH | 0 | KWH | 1931426 | KWH | OTHER | Normal | 0 | KW | 83 | M3 | CATEGORY_1 | 83 | M3 | 0 | KWH | 27 | DEGREE_CELSIUS | 21.6 | DEGREE_CELSIUS | OTHER | R1234ZE, R407C, R410A | 39 | DEGREE_DAYS | 342622 | KWH | 262674 | KWH | 0 | KWH | 79948 | KWH
NL-NL-6199 | Datacenter Maastricht |  | Datacenter Maastricht | GM0888 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2009 | July | 2N | AT_RACK_LEVEL | 2N | AT_ROOM_LEVEL | 650 | KW | RATED | 5500 | M2 | 2077 | M2 | 7709680 | KWH | 51466 | KWH | 5675363 | KWH | OTHER |  | 552 | KW | 15175 | M3 | CATEGORY_1 | 15175 | M3 | 0 | KWH | 25.1 | DEGREE_CELSIUS | 22.5 | DEGREE_CELSIUS | R_134A |  | 69 | DEGREE_DAYS | 7709680 | KWH | 7358080 | KWH | 0 | KWH | 351600 | KWH
NL-NL-Ah-Pts | KPN BV |  | Arnhem | GM0202 | Ja | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE | 2019 | October | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL | 678 | KW | RATED | 7095 | M2 | 3144 | M2 | 8286960 | KWH | 0 | KWH | 5795076 | KWH | OTHER | Geen functie | 0 | KW | 24 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_410A |  | 0 | DEGREE_DAYS | 8690833 | KWH | 7734841 | KWH | 955992 | KWH | 0 | KWH | 100% groen, 89% van totale energieconsumptie uit stroomovereenkomst, 11% uit PPA.
NL-NL-Ap-Fs | KPN BV |  | Apeldoorn | GM0200 | Nee | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE | 1990 | January
NL-NL-Asd-Drs | KPN BV |  | Amsterdam | GM0363 | Ja | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE | 2018 | January | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL | 1961 | KW | RATED | 36847 | M2 | 14041 | M2 | 23585821 | KWH | 0 | KWH | 17215928 | KWH | OTHER | Geen functie | 0 | KW | 3000 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_134A |  | 0 | DEGREE_DAYS | 23574946 | KWH | 2593244 | KWH | 20981702 | KWH | 0 | KWH | 100% groen, 89% van totale energieconsumptie uit stroomovereenkomst, 11% uit PPA.
NL-Nl-Hlm-Wdp | KPN BV |  | Haarlem | GM0392 | Nee | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE | 1990 | January
NL-nlrtm1 | Smartdc B.V. |  | Smartdc Rotterdam 1 | GM0599 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2009 | August | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 1800 | KW | INSTALLED | 3500 | M2 | 1653 | M2 | 15868205 | KWH | 0 | KWH | 11075588 | KWH | OTHER | We don't do anything special with the grid. | 0 | KW | 0 | M3 | CATEGORY_1 | 238 | M3 | 3650000 | KWH | 70 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | OTHER | R_1234ZE | 3168 | DEGREE_DAYS | 15868205 | KWH | 0 | KWH | 0 | KWH | 0 | KWH
NL-NL-Rt-Wah | KPN BV |  | Rotterdam | GM0599 | Ja | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE | 2021 | March | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL | 2051 | KW | RATED | 39992 | M2 | 11769 | M2 | 25255080 | KWH | 0 | KWH | 17911404 | KWH | OTHER | Geen functie | 0 | KW | 39662 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 27 | DEGREE_CELSIUS | R_134A |  | 0 | DEGREE_DAYS | 26894278 | KWH | 23935907 | KWH | 2958371 | KWH | 0 | KWH | 100% groen, 89% van totale energieconsumptie uitstroomovereenkomst, 11% uit PPA. | 0 | THOUSANDS | 0 | PB
NL-nLT-AMS1 | EI Data Center Netherlands BV |  | AMS1/Gyroscoopweg | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | October | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 450 | KW | RATED | 2100 | M2 | 1100 | M2 | 5269360 | KWH | 2261 | KWH | 3704211 | KWH | OTHER | geen | 1100 | KW | 0 | M3 | CATEGORY_1 | 320 | M3 | 0 | KWH | 29 | DEGREE_CELSIUS | 25 | DEGREE_CELSIUS | R_410A |  | 74 | DEGREE_DAYS | 5269360 | KWH | 5269360 | KWH | 0 | KWH | 0 | KWH | AMS1 gebruikt geen koelwater systeem | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-nLT-AMS2 | EI Data Center Netherlands BV |  | AMS2/Koolhovenlaan | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2024 | April | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 960 | KW | RATED | 3600 | M2 | 1444 | M2 | 11639275 | KWH | 5000 | KWH | 7759517 | KWH | PEAK_DEMAND |  | 900 | KW | 600 | M3 | CATEGORY_1 | 600 | M3 | 0 | KWH | 18 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | R_407C |  | 74 | DEGREE_DAYS | 5919000 | KWH | 5919000 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-NTT-AMS1 | NTT Global Data Centers Netherlands B.V. | dc.emea.sustainability@global.ntt | AMS1 | GM0394 | Ja | COLOCATION_DATA_CENTRE_GROUP_OF_STRUCTURES | 2019 | July | 2N | AT_HIGH_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 20700 | KW | INSTALLED | 29219 | M2 | 7702 | M2 |  |  | 70955 | KWH | 111132566 | KWH | OTHER | None | 0 | KW | 6265 | M3 | CATEGORY_2 | 6265 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | OTHER | R134A, R410A, R513A, R452B | 17 | DEGREE_DAYS | 0 | KWH | 0 | KWH | 0 | KWH | 0 | KWH
NL-NWG-01 | NorthC Datacenters B.V. |  | NorthC Nieuwegein | GM0356 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2002 | May | 2N | AT_RACK_LEVEL | N+1 | AT_RACK_LEVEL |  |  | INSTALLED | 8005 | M2 | 4075 | M2 | [6 empty] | OTHER | NVT | 0 | KW |  |  | CATEGORY_1 | 10658 | M3 | 0 | KWH | 28.4 | DEGREE_CELSIUS | 25.7 | DEGREE_CELSIUS | R_410A |  | 29 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons niet bekend.
NL-Odi | Odido Netherlands B.V. |  | POP AMS2 | GM0363 | Ja | ENTERPRISE_DATA_CENTRE_SINGLE_STRUCTURE | 1999 | October | [34 empty] | 365 | DEGREE_DAYS
NL-OIB-15-034 | SSC-ICT |  | OIB.15.034 | GM0603 | Ja | ENTERPRISE_DATA_CENTRE_SINGLE_STRUCTURE | 2014 | November | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 3000 | KW | INSTALLED |  |  |  |  | 10678505 | KWH | 0 | KWH | 7500000 | KWH | OTHER | Backup alleen voor interne continuiteit | 0 | KW | 6500 | M3 | CATEGORY_2 | 6000 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 23.5 | DEGREE_CELSIUS | R_729 |  | 49 | DEGREE_DAYS | 10678505 | KWH | 10678505 | KWH | 0 | KWH | 0 | KWH | nvt
NL-OUM-01 | NorthC Datacenters B.V. |  | NorthC Oude Meer | GM0394 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 1990 | January | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL |  |  |  | 18000 | M2 | 6200 | M2 | [6 empty] | OTHER | Geen | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 23.4 | DEGREE_CELSIUS |  |  | R_134A |  | 34 | DEGREE_DAYS |  |  |  |  | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons onbekend.
NL-PDC1 | Previder BV | e.tielman@previder.nl | PDC1 | GM0164 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2013 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 530 | KW | RATED | 11000 | M2 | 4500 | M2 | 5703451 | KWH | 0 | KWH | 4633451 | KWH | PEAK_DEMAND |  | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 18 | DEGREE_CELSIUS | 21 | DEGREE_CELSIUS | R_134A |  | 155 | DEGREE_DAYS | 0 | KWH | 0 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 80 | PERCENT | 0 | PERCENT | 9.9 | GB | 11.2 | GB | 0.1 | EB | 0.1 | EB
NL-PDC2 | Previder BV | e.tielman@previder.nl | PDC2 | GM0164 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2010 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 730 | KW | RATED | 2500 | M2 | 1600 | M2 | 8431180 | KWH | 0 | KWH | 6720180 | KWH | PEAK_DEMAND |  | 0 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 18 | DEGREE_CELSIUS | 22 | DEGREE_CELSIUS | R_134A |  | 155 | DEGREE_DAYS | 660685 | KWH | 0 | KWH | 0 | KWH | 660685 | KWH |  | 0 | THOUSANDS | 0 | PB | 80 | PERCENT | 0 | PERCENT | 9.9 | GB | 11.2 | GB | 0.1 | EB | 0.1 | EB
NL-RTD1 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter Rotterdam 1 | GM0482 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2011 | March | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 748 | KW | RATED | 4900 | M2 | 1800 | M2 | 8203000 | KWH | 21034 | KWH | 5661240 | KWH | PEAK_DEMAND |  | 2400 | KW | 716 | M3 | CATEGORY_1 | 716 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 0 | DEGREE_CELSIUS | R_410A |  | 112 | DEGREE_DAYS | 8203000 | KWH | 8203000 | KWH | 8203000 | KWH | 0 | KWH | - | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-RTD2 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter Rotterdam 2 | GM0599 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2009 | March | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 537 | KW | RATED | 3500 | M2 | 1200 | M2 | 6284449 | KWH | 14400 | KWH | 1643447 | KWH | PEAK_DEMAND |  | 1758 | KW | 732 | M3 | CATEGORY_1 | 732 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 0 | DEGREE_CELSIUS | R_407C |  | 34 | DEGREE_DAYS | 6284449 | KWH | 6284449 | KWH | 6284449 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-RTM-02-03 | NorthC Datacenters B.V. |  | NorthC Rotterdam Zestienhoven | GM0599 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2014 | April | 2N | AT_RACK_LEVEL | N+1 | AT_RACK_LEVEL |  |  | INSTALLED | 7461 | M2 | 4214 | M2 | [6 empty] | OTHER | NVT |  |  |  |  | CATEGORY_1 |  |  | 0 | KWH | 26.7 | DEGREE_CELSIUS | 26.4 | DEGREE_CELSIUS | R_407C |  | 29 | DEGREE_DAYS | [9 empty] | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB | Voor ons niet bekend.
NL-RU-EOS | Stichting Radboud Universiteit |  | EOS | GM0268 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 2010 | September | [45 empty] | 0 | THOUSANDS | 0 | PB | 80 | PERCENT | 45 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-RU-Forum | Stichting Radboud Universiteit |  | Forum | GM0268 | Ja | ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES | 1990 | September | [45 empty] | 0 | THOUSANDS | 0 | PB |  |  |  |  | 0 | GB | 0 | GB |  |  | 0 | EB
NL-SFRDC-AMS1 | Serverfarm Global NL B.V. |  | AMS1 | GM0363 | Ja | COLOCATION_DATA_CENTRE_GROUP_OF_STRUCTURES | 2016 | October
NL-SL-A | SkyLink Data Center BV | info@skylink-data-center.nl | SkyLink Data Center BV | GM0928 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2023 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 400 | KW | INSTALLED | 500 | M2 | 350 | M2 | 5400000 | KWH | 0 | KWH | 4406400 | KWH | PEAK_DEMAND |  | 750 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 31 | DEGREE_CELSIUS | 26 | DEGREE_CELSIUS | R_454B |  | 155 | DEGREE_DAYS | 6570000 | KWH | 6570000 | KWH | 6570000 | KWH | 6570000 | KWH
NL-SL-B | SkyLink Data Center BV | info@skylink-data-center.nl | SkyLink Data Center BV | GM0928 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2018 | January | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 500 | KW | INSTALLED | 500 | M2 | 400 | M2 | 5431200 | KWH | 0 | KWH | 1051200 | KWH | PEAK_DEMAND |  | 660 | KW | 0 | M3 | CATEGORY_1 | 0 | M3 | 0 | KWH | 31 | DEGREE_CELSIUS | 26 | DEGREE_CELSIUS | R_454B |  | 155 | DEGREE_DAYS | 5431200 | KWH | 5431200 | KWH | 5431200 | KWH | 317000 | KWH
NL-Switch2 | Switch datacenters Amsterdam 2 B.V. |  | AMS2 | GM0632 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2014 | January | 2N | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL | 800 | KW | INSTALLED | 5723 | M2 | 1462 | M2 | 3433136 | KWH | 0 | KWH | 2219670 | KWH | OTHER | N/A | 0 | KW | 2461 | M3 | CATEGORY_2 | 2461 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 22 | DEGREE_CELSIUS | OTHER | Water | 53 | DEGREE_DAYS | 3433136 | KWH | 3433136 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-Switch3 | Switch Datacenters Amsterdam 3 B.V. |  | AMS3 | GM0363 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2017 | January | N+1 | AT_RACK_LEVEL | N+1 | AT_ROOM_LEVEL | 2950 | KW | INSTALLED | 10900 | M2 | 5000 | M2 | 25451400 | KWH | 0 | KWH | 21144070 | KWH | OTHER | N/A | 0 | KW | 27041 | M3 | CATEGORY_1 | 27041 | M3 | 0 | KWH | 28 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | OTHER | Water | 26 | DEGREE_DAYS | 25451400 | KWH | 25451400 | KWH | 0 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-SWT | Swift |  | Swift | GM0638 | Ja | ENTERPRISE_DATA_CENTRE_SINGLE_STRUCTURE | 1990 | January
NL-THG1-DFDC | Data Facilities The Hague B.V. | sales@dfdc.io | Data Facilities The Hague | GM0518 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2014 | December | 2N+1 | AT_LOW_VOLTAGE_LEVEL | 2N+1 | AT_ROOM_LEVEL | [9 empty] | 0 | KWH |  |  |  |  | 0 | KW |  |  | CATEGORY_1 |  |  | 0 | KWH | 35 | DEGREE_CELSIUS | 24 | DEGREE_CELSIUS | R_410A |  | 16 | DEGREE_DAYS | [6 empty] | 0 | KWH
NL-TUD-DC1 | ICT-SSC Infra |  | DC IO | GM0503 | Ja | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE_WITH_COLOCATION_SERVICES | 2006 | January
NL-TUD-DC2 | ICT-SSC Infra |  | DC RID | GM0503 | Ja | CO_HOSTING_DATA_CENTRE_SINGLE_STRUCTURE_WITH_COLOCATION_SERVICES | 2008 | January
NL-UTR1 | Eurofiber Cloud Infra B.V. | corporate.compliance@eurofiber.com | Eurofiber Datacenter Utrecht 1 | GM0310 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE_WITH_CO_HOSTING_SERVICES | 2012 | April | N+1 | AT_LOW_VOLTAGE_LEVEL | N+1 | AT_ROOM_LEVEL | 949 | KW | RATED | 3500 | M2 | 2000 | M2 | 10991000 | KWH | 28800 | KWH | 7957060 | KWH | PEAK_DEMAND |  | 2500 | KW | 452 | M3 | CATEGORY_1 | 452 | M3 | 0 | KWH | 0 | DEGREE_CELSIUS | 0 | DEGREE_CELSIUS | R_410A |  | 112 | DEGREE_DAYS | 10991000 | KWH | 10991000 | KWH | 10991000 | KWH | 0 | KWH |  | 0 | THOUSANDS | 0 | PB | 0 | PERCENT | 0 | PERCENT | 0 | GB | 0 | GB | 0 | EB | 0 | EB
NL-WP | ING |  | ING Wilgenplas | GM0599 | Ja | ENTERPRISE_DATA_CENTRE_SINGLE_STRUCTURE | 1991 | January | [24 empty] | 27162 | M3 | [31 empty] | 0.1 | EB | 0.1 | EB
NL-ZW1 | Equinix Netherlands BV | compliance-nl@eu.equinix.com | ZW1 | GM0193 | Ja | COLOCATION_DATA_CENTRE_SINGLE_STRUCTURE | 2008 | February | N+1 |  | N+1 |  |  |  |  | 1600 | M2 | 900 | M2 | [13 empty] | 151 | M3